Department of Public Works

City of Newton

Setti D. Warren

Mayor

Utilities Division

# Cross Connection Control Program

# 60 Elliot Street

Newton, Ma. 02461

Telephone (617) 796-1658     Fax (617) 965-5898

## City of Newton Standards for Fire Service/Backflow Device Installation

A Completed Design Data Sheet with an 8.5” X 11” Engineered Drawing (showing the details listed on the Backflow Prevention Device Design Data Sheet) must be submitted and approved by the City of Newton’s Cross Connection Control Program office located at 60 Elliot Street Newton, MA 02461 prior to installation of the backflow device.

ALL connections from the foundation/wall to the backflow device must be mechanical flange to flange factory welded.

A Flange to Flange spool piece for a low pressure switch must be installed between the flanged spool piece at the foundation wall/floor and the OS&Y valve in addition to the Backflow Device gate valves.

Pipes must be restrained to the wall/floor at the point of entry into to building with a minimum of ½” threaded restraining rods.

Backflow device must be a minimum 3’ from the floor and a minimum 12” from any adjacent wall.

(Device must be accessible for testing.)

The Cross Connection Control Technician will inspect the installation after the disinfection and pressure tests have been completed. Should the backflow device test fail, it must be repaired within 14 days from notification of failure.

Chlorination and Pressure Tests, are the responsibility of the OWNER.

The City reserves the right to determine the date and time of testing

All applicable permits must be obtained from the Newton Fire Department and Newton Inspectional Services Department, said permits will forwarded to the Cross Connection Control Program office prior to installation, inspection and testing.